## EC Fans
CENTRIFUGAL FAN SECTION : FRESH AIR FAN SECTION
S.No. | Description | Unit | Quantity | Rate (Rs.) | Amount (Rs.)
a) | Supply, installation, testing, commissioning of, Fan section consist of Centrifugal Fan, backward curved, Electronically commutated fan, consisting of integrated fan and motor assembly of 415 +/- 10% volts, 3 Phase, 50 Hz.with electronically commutated plug fan. The motor shall be a permanent magnet external rotor motor with integrated electronics and suitable for continuous operation. The minimum efficiency class of the motor shall be equivalent to IE4 with a certification from a NABL approved laboratory. The speed of the motor shall be variable depending on an external control signal of 0-10V. The fans shall be Modbus RTU compatible for communication with BMS (Building Management System). The fan in totality shall be of most efficient type so that the power consumption and noise level is minimal. The motor shall be minimum IP54 protection class, with Thermal class 155 (Insulation class F). The EC motor shall be provided with suitable protection from moisture & hot climate. The impeller and fan shaft shall be statically and dynamically trim balanced to ISO 1940 grade. EC Motor shall be integrated with a separate controller for speed modulation of fans. Fan characteristic curves shall be related to measurements on a fan test rig with inlet silencing chamber in accordance with relevant standard.Motor shall have Locked Rotor Protection,Thermal Protection,Less and Excessive Voltage Protection,Overcurrent Protection and Soft start. The motor rating shall be 20% greater than the shaft load.All fans shall be factory fabricated only and shall be selected for the lowest operating noise level. High efficiency, Capacity ratings, Low power consumption, with operating points clearly indicated, shall be submitted and verified at the time of testing and commissioning of the installation.The fan shall be SISW as per the best selection Centrifugal Impeller with High Efficiency Backward curved blades and external rotor EC (Electronically Commutated) motor, energy optimized for operation without spiral housing for high efficiency and favorable acoustic behavior. The high efficiency backward curved impeller with rotating diffuser, made of high-performance welded aluminum sheet material, with external rotor motor balanced together statically and dynamically according to relevant standard. Fans shall be CE certified. The EC fan should be capable of being fitted in horizontal or vertical position in the fan section, depending on the application. The inlet cone shall be provided with a nozzle for volume flow measurement of the fan.The fan impeller shall be mounted on a solid shaft supported to housing with angle iron frame and heavy-duty ball bearings. Blanking sheets to be provided in front of each fan section to isolate and prevent backflow during maintenance or non-operation times.The complete EC Fan unit shall be of rugged bolted construction made of sheet steel, statically and dynamically balanced. The supply air fan shall have its performance certified from a NABL accredited laboratory within India. The EC fan should carry a warranty of a 18 months from the date of delivery.