## IAQ Monitor
IAQ Monitors
S.No. | Description |  |  |  | Unit | Quantity | Rate (Rs.) | Amount (Rs.)
a) | The deployment of the Indoor Air Quality (IAQ) monitoring system is designed to meet WELL compliance standards, ensuring optimal environmental health and comfort. Each unitized room will be equipped with a WELL-compliant IAQ monitor. Sensor placement will be aligned with WELL rating system recommendations to ensure accuracy and effective monitoring. These monitors will measure critical environmental parameters, including Carbon Dioxide (CO₂), Particulate Matter (PM1, PM2.5, PM4, and PM10), Total Volatile Organic Compounds (TVOCs), Temperature, and Humidity, providing a comprehensive understanding of indoor air quality. All sensors will connect via Wi-Fi to a centralized backend system, enabling seamless data transmission and real-time visualization of IAQ metrics across all monitored spaces. A user-friendly dashboard will display this data, allowing for easy monitoring and management. Furthermore, the system will store historical data on the cloud for up to 15 days, facilitating trend analysis and reporting. This integrated approach ensures a robust and reliable IAQ monitoring solution tailored to meet WELL certification requirements.
b) | The monitor will be wall mount type ( “plug-n-play”) with an LED backlit touch display of at least 4 inches with a 720X resolution. It will be able to transmit data using RS485 port and connect to WiFi and transmit data to a cloud monitoring server to store data. The backend software allows for rule-based alerts given to the operatorThe backend software must include advanced features, such as rule-based alert functionality, allowing operators to define specific thresholds and triggers for various parameters. This combination of robust hardware and intelligent software capabilities ensures a flexible, efficient, and future-proof monitoring solution. Air Quality monitors will operate on 5.0V power supply and peak power consumption should not be more than 7.5 watts. These monitors are designed and manufactured in INDIA using high quality sensors from Europe/USA/UK. The device is WELL compliant. The device allows for lacquered glass front fascia to provide colors as per choice of the customer.
c) | The accuracies of the sensors need to be as follows:
| Description | Parameters | Measuring Range | Accuracy
| Particle Measurement | PM 1.0 | 0-1000 ug/m3 | [5 μg/m3 + 5 % m.v.] at values between 0 and 100 μg/m³.
+10% @ 101-1000 ug/m3.
|  | PM 2.5 | 0-1000 ug/m3 | [5 μg/m3 + 5 % m.v.] at values between 0 and 100 μg/m³.
+/- 10% @ 101-1000 ug/m3.
|  | PM 4.0 | 0-1000 ug/m3 | +/- 25 μg/m3 at values between 0 and 100 μg/m³.
+/- 25% @ 101-1000 ug/m3.
|  | PM 10 | 0-1000 ug/m3 | +/- 25 μg/m3 at values between 0 and 100 μg/m³.
+/- 25% @ 101-1000 ug/m3.
| Carbon Di-oxide | CO2 | 0-5000 ppm | Accuracy ± (50 ppm + 2.5%) of reading at values between 400 and 1000 ppm.
±(50 ppm + 3%) of reading at values between 1001 and 2000 ppm
±(40 ppm + 5%) of reading at values between 2001 and 5000 ppm
| Total VOC | TVOC | 1-580,000 ppb | Accuracy (+/- 20% + 15%) ppb of reading of measured value.
| Temperature | Temp | -40 - 125 °C | Typical +/- 0.20 °C.
| Humidity | RH | 0-100% | Typical +/- 1.8% RH.