## Thermostat
IAQ Monitors
S.No. | Description |  |  |  | Unit | Quantity | Rate (Rs.) | Amount (Rs.)
a) | The modulating thermostat shall incorporate advanced features to deliver precise control of building parameters. It shall support a modulating output signal (0-10V) for fan operation and include On/Off or modulating output signal (0-10V) for valve control, ensuring optimized heating and cooling performance. The thermostat shall feature a compact design suitable for retrofitting into a standard 4 x 3 J-box for easy installation. It must include a LED backlit 4-inch capacitive screen with a resolution of 480 x 480, offering a clear and user-friendly interface. The thermostat shall be Wi-Fi enabled for seamless integration and connectivity, with over-the-air (OTA) firmware updates to ensure continuous performance enhancement and feature upgrades. The sensors used in the thermostat shall meet U.S. or European standards to ensure high-quality performance and reliability.Aesthetically, the thermostat shall be available in preferred color options to complement interior design preferences. It must be CE certified, adhering to international safety and performance standards. Additionally, the thermostat shall enable real-time access to sensor data and allow remote monitoring and control of building parameters through a proprietary building intelligence platform. The product must be designed and manufactured in India, promoting local innovation and development.The vendor shall provide installation and commissioning services in accordance with the project timeline. The thermostats must carry a minimum warranty of 12 months from the date of commissioning.All offered products must strictly comply with the specified requirements, and any deviations shall be clearly stated in the tender submission along with alternative proposals for consideration. The vendor must submit detailed technical documentation, including product datasheets and sensor manufacturer with accuracy readings
b) | The accuracies of the sensors need to be as follows:
| Description | Parameters | Measuring Range | Accuracy
| Temperature | Temp | -40 - 125 °C | Typical +/- 0.20 °C.
| Humidity | RH | 0-100% | Typical +/- 1.8% RH.